### AI Observations, Flags & Insights (The "Demo" View)

(These are the "smart" alerts the platform would display to the user to prevent mistakes)

#### 🔴 Critical Risk Flags (High Priority)

- Warranty Conflict Resolved [Addendum 2]:

  - Insight: "Drawings listed generic coverboard. Addendum 2 explicitly requires 5/8" GP Dens Deck to achieve the 20-year/120mph warranty. Ensure your bid reflects this specific material cost, not generic pricing."

- Electrical Load Mismatch [Addendum 1 - Mech Review]:

  - Insight: "Engineer notes that submitted equipment loads for RTU-1 through RTU-5 exceed basis of design. Electrical Contractor must coordinate breaker/wire sizing carefully. Potential Change Order risk if not caught now."

- Field Fabrication Required [Addendum 1]:

  - Insight: "RTU-5 Curb cannot be a standard factory curb. Addendum 1 requires field fabrication. Labor hours for this item should be increased."

#### 🟡 Scope Clarifications (Medium Priority)

- Controls Scope Reduction [Addendum 1]:

  - Insight: "Spec M0.2 originally referenced a DDC system. Addendum 1 deletes this. Scope is now limited to factory controls and wall timers. Do not carry cost for full DDC integration."

- Unknown Utilities [Spec 33 41 00]:

  - Insight: "Civil spec notes subsurface investigations were not performed. Clause 1.01.B places risk on Contractor. Recommend carrying a contingency for 'Unsuitable Soils'."

- Asphalt Temperature Limit [Spec 32 12 16]:

  - Insight: "Paving restricted to ambient air > 32°F and rising. Verify schedule feasibility for Kenai, AK location."

#### 🔵 Commercial Insights (Low Priority / Strategy)

- Liquidated Damages:

  - Insight: "Confirmed at $300/day [Agreement Art. 11]. Schedule is 300 calendar days."

- Approved Substitutions:

  - Insight: "York and Rupp Air approved as alternates to Daikin. Check pricing for potential savings."

- Tax Compliance:

  - Insight: "Kenai Peninsula Borough tax compliance required. Ensure registration to collect sales tax [ITB Page 19]."