## work packages - high level
ID | Trade | Work Package / Item | Action | Specifications / Quantities | Source Ref
CIV-01 | Civil | Roof Drain Field #1 | Install New | 30'L x 15'W x 3.5'D excavation; (3) 24" ADS laterals; Backfill w/ drain rock | [Sheet C1.0, C2.0] | note: full breakdown list of each trade in a sperate tab (running AI deep mode)
CIV-02 | Civil | Roof Drain Field #2 | Install New | 12'L x 4'W x 3.5'D excavation; (1) 24" ADS lateral | [Sheet C1.0, C3.0]
CIV-03 | Civil | Concrete Sidewalk | Remove & Replace | 4" Concrete w/ W1.4xW1.4 mesh; 4' wide; Match existing grade | [Sheet C1.0, C3.0]
CIV-04 | Civil | Asphalt Pavement | Patching | Sawcut clean edge; Repave & grade to match drainage; Paint edges w/ hot asphalt | [Sheet C2.0]
CIV-05 | Civil | Monitoring Pipes | Install New | (3) 4" SCH40 ABS pipes per field; Connect to CPEP w/ Fernco | [Sheet C2.0]
CIV-06 | Civil | Insulation Board (Civil) | Install | 4" Insulfoam 40 Expanded Polystyrene (over drain fields) | [Sheet C2.0]
ARC-01 | Arch | Low Slope Roofing (Roofs A-H) | Demo | Remove existing BUR, coverboard, and tapered insulation at crickets | [Sheet A1.1]
ARC-02 | Arch | Low Slope Roofing (Roofs A-H) | Install New | New Roof System per spec; 5/8" Coverboard; 5/8" Sheathing | [Sheet A1.2, A2.3]
ARC-03 | Arch | Parapet Flashing | Replace | New 24ga pre-finished metal flashing & counter flashing; 1x8 composite trim | [Sheet A1.2, A2.1]
ARC-04 | Arch | Roof Access Hatch | Install New | 30" x 54"; Install at existing opening; Provide safety rails/ladder up-posts | [Sheet A1.2]
ARC-05 | Arch | Roof Ladder | Replace | Remove existing; Install new ladder per spec (See Detail 6,7/A2.3) | [Sheet A1.2]
ARC-06 | Arch | Scuppers | Replace/New | Demo existing; Install new per Detail 5/A2.3 (Roof B specific notes) | [Sheet A1.2]
ARC-07 | Arch | Wood Fencing | Demolish | Demo existing wood privacy fence | [Sheet A1.1]
ARC-08 | Arch | Walking Pads | Install | Rubber walking pads from hatch to ladder and equipment | [Sheet A1.2]
ARC-09 | Arch | Tapered Insulation | Install | New tapered insulation crickets (1/2" per 12" slope) | [Sheet A1.2]
MEC-01 | Mech | RTU-1 (Raquetball) | Replace | 4 Ton; Daikin 048; Gas/Electric; 1600 CFM | [Sheet M0.1]
MEC-02 | Mech | RTU-2 (Cardio) | Replace | 3 Ton; Daikin 036; Gas/Electric; 1200 CFM | [Sheet M0.1]
MEC-03 | Mech | RTU-3 (2nd Fl Commons) | Replace | 8.5 Ton; Daikin 102; Gas/Electric; 3500 CFM | [Sheet M0.1]
MEC-04 | Mech | RTU-4 (Lobby/Weight) | Replace | 8.5 Ton; Daikin 102; Gas/Electric; 3500 CFM | [Sheet M0.1]
MEC-05 | Mech | RTU-5 (Locker Rooms) | Replace | 7.5 Ton; Daikin 090; Gas/Electric; 2610 CFM | [Sheet M0.1]
MEC-06 | Mech | RTU-6 (Gym) | Replace | 20 Ton; Daikin 240; Gas/Electric; 7950 CFM | [Sheet M0.1]
MEC-07 | Mech | Exhaust Fan EF-1 | Replace | Ceiling Mount; 200 CFM; Greenheck SP-A290 | [Sheet M0.1]
MEC-08 | Mech | Exhaust Fan EF-2 | Replace | Ceiling Mount; 200 CFM; Greenheck SP-A290 | [Sheet M0.1]
MEC-09 | Mech | Exhaust Fan EF-3 | Replace | Inline; 400 CFM; Greenheck BSQ-80-4 | [Sheet M0.1]
MEC-10 | Mech | Exhaust Fan EF-4 | Replace | Roof Direct; 720 CFM; Greenheck USF-13 | [Sheet M0.1]
MEC-11 | Mech | Exhaust Fan EF-5 | Replace | Roof Direct; 6280 CFM; Greenheck USF-20 | [Sheet M0.1]
MEC-12 | Mech | Roof Curbs | Install New | Insulated roof curbs for RTUs (24" high); Coordinate w/ Structural | [Sheet M2.3]
MEC-13 | Mech | Gas Piping (Roof) | Replace | Black steel; New supports; Connect to RTUs | [Sheet M2.3]
MEC-14 | Mech | Exterior Ductwork | Install | Q-Duct (Pre-insulated phenolic); R-12; Weatherproof | [Sheet M0.2]
MEC-15 | Mech | Doghouse Penetration | Install | 32"x32"x24" high insulated doghouse for ductwork | [Sheet M2.3]
PLU-01 | Plumb | Roof Drains (RD-1) | Install New | Cast iron dome; Underdeck clamp; 3" connection | [Sheet M0.1, C1.0]
PLU-02 | Plumb | Overflow Drains (OD-1) | Install New | 2" water dam collar; Underdeck clamp | [Sheet M0.1]
PLU-03 | Plumb | Rain Leaders | Install | 3" & 4" piping; Cast Iron (No-Hub) or ABS (allowed concealed) | [Sheet M2.2, M0.2]
PLU-04 | Plumb | Heat Trace | Install | Electric heat trace in rain leaders/overflows | [Sheet C1.0]
ELE-01 | Elec | Panel 'X' | Demolish | Remove panel, feeders, and conduits back to source | [Sheet E1.0]
ELE-02 | Elec | Panel 'D' | Install New | Relocate circuits from 'X'; Install new panel | [Sheet E1.0]
ELE-03 | Elec | Main Breaker | Replace | Replace existing 300A main w/ New 400A Main Breaker | [Sheet E4.0]
ELE-04 | Elec | Panel Feeders | Replace | New feeder to Panel 'A'; New feeder to Panel 'MECH' | [Sheet E4.0]
ELE-05 | Elec | Duct Smoke Detectors | Install | Provide audio/visual alarm at check-in counter | [Sheet E3.0]
ELE-06 | Elec | Heat Trace Connection | Install | Power connection for rain leader heat trace (Tyco/Raychem) | [Sheet E4.0]

## General Requirements & Site Con
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
GEN-01 | General | Construction Permits | Admin | Arrange and pay for all permits and inspections | [Sheet M0.2]
GEN-02 | General | As-Built Verification | Verify | Field verify existing roof slopes, elevations, dimensions | [Sheet A1.1 Note 3]
GEN-03 | General | Protection of Work | Protect | Protect existing finishes; Repair damages to lawns/site elements | [Sheet A1.1 Note 10]
GEN-04 | General | Hazardous Materials | Abate | Remove VTRs containing lead caps (Lead Awareness required) | [Sheet A1.1 Note 7]
GEN-05 | General | Testing & Balancing | Service | Independent air balancing (SMACNA) for HVAC systems | [Sheet M0.2]
GEN-06 | General | O&M Manuals | Submit | Include warranty certificates and supplier contacts | [Sheet M0.2]
Bid Form
Flooring:
Luxury Vinyl Tile [Reference Detail 7 / Sheet A-606}
[8 empty] | Person Responsible |  |  |  | Luxury Vinyl Tile [Reference Detail 7 / Sheet A-606}
|  |  |  | 4-wk Effort |  | Day 0 | Building Connected Invite Sent Out | Precon Lead
Subcontractors Notified
[7 empty] | assigned Scope Captains | Scope Captains | Decided by Preconstruction Director / VP or Equal
Drawings / Documents / Specs all populated on Day 0
[6 empty] | Week 1 | Building out bid forms | Scope Captains per Scope |  | 6-8 perb
[7 empty] | Outlining all scope pertinent to bid form | ""
Calling Subcontracotrs
[6 empty] | Week 2 | Pre-Bid RFIs Due | Populated by Scope Captains
[6 empty] | Week 3 | Pre-Bid RFIs are returned by Design Team | Typically 1-wk to respond - Design Team
[6 empty] | Week 4 | Everything is due

## Civil & Site Work
ID | Trade | Scope Responsible | Work Package / Item | Action | Specifications / Notes | Source Ref
CIV-01 | Civil | Asphalt Paving | Asphalt Pavement | Sawcut | Sawcut clean edge on existing pavement | [Sheet C1.0] | Sawcut [Sheet C1.0] | Asphalt Paving:
CIV-02 | Civil | Asphalt Paving | Asphalt Pavement | Demo | Remove 12" additional asphalt from cut edge | [Sheet C2.0 Note 3] | Demo [Sheet C2.0 Note 3] |  | Demo [Sheet C2.0 Note 3]
CIV-03 | Civil | Asphalt Paving | Asphalt Pavement | Install | Type IIA; Match existing drainage; Paint edges w/ hot asphalt | [Sheet C2.0] | Install [Sheet C2.0] |  | Install [Sheet C2.0]
CIV-04 | Civil | Earthworker | Excavation (Drain Field #1) | Excavate | 30'L x 15'W x 3.5'D; Slope per OSHA standards | [Sheet C1.0] | Excavate [Sheet C1.0] |  | Excavate [Sheet C1.0]
CIV-05 | Civil | Earthworker | Excavation (Drain Field #2) | Excavate | 12'L x 4'W x 3.5'D; Slope per OSHA standards | [Sheet C1.0] | Excavate [Sheet C1.0]
CIV-06 | Civil | Landscaper | Drain Rock | Install | Coarse grade washed drain rock (backfill around pipes) | [Sheet C2.0] | Install [Sheet C2.0]
CIV-07 | Civil | Landsacper | Geotextile Fabric | Install | Typar 3401 or approved alternative (on top of rock) | [Sheet C2.0] | Install [Sheet C2.0]
CIV-08 | Civil | Waterproofer | Insulation Board (Site) | Install | 4" Insulfoam 40 Expanded Polystyrene (drain fields) | [Sheet C2.0] | Install [Sheet C2.0]
CIV-09 | Civil |  | Backfill | Install | NFS Sand/Gravel; Compact to 95% density | [Sheet C2.0 Note 1] | Install [Sheet C2.0 Note 1]
CIV-10 | Civil |  | Topsoil & Seeding | Install | 4" Topsoil; Regrade to maintain drainage | [Sheet C1.0] | Install [Sheet C1.0]
CIV-11 | Civil |  | Concrete Sidewalk | Remove | Remove existing sidewalk at Bidarka St | [Sheet C1.0] | Remove [Sheet C1.0]
CIV-12 | Civil |  | Concrete Sidewalk | Pour | 4" thick; 3000 PSI; W1.4xW1.4 mesh; Broom finish | [Detail B/C3.0] | Pour [Detail B/C3.0]
CIV-13 | Civil |  | Warning Tape | Install | Vinyl warning tape (18" above pipe) | [Sheet C3.0] | Install [Sheet C3.0]
31 00 00 - Asphalt Paving:
Sawcut clean edge on existing pavement [Sheet C1.0]
Remove 12" additional asphalt from cut edge [Sheet C2.0 Note 3]
32 16 00 - Curbs, Gutters, Sidewalks, and Driveways
Type IIA; Match existing drainage; Paint edges w/ hot asphalt [Sheet C2.0]
Asphalt PaVement:

## Architectural - Demolition
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
ARC-01 | Demo | Built-Up Roofing (BUR) | Demolish | Remove BUR, cant strips, and tapered insulation | [Sheet A1.1 Note 1]
ARC-02 | Demo | Parapet Coping | Demolish | Remove coping and associated hardware | [Detail 1/A2.1]
ARC-03 | Demo | Roof Scuppers | Demolish | Remove existing scuppers (Save Roof B for replacement) | [Sheet A1.1 Note 6]
ARC-04 | Demo | Roof Ladder | Demolish | Remove existing access ladder | [Sheet A1.1 Note 5]
ARC-05 | Demo | Wood Fence | Demolish | Remove wood privacy fence | [Sheet A1.1 Note 8]
ARC-06 | Demo | 2x4 Sleepers | Demolish | Remove sloped 2x4 sleepers (Roof D) | [Sheet A1.1 Note 9]
ARC-07 | Demo | Sheathing | Demolish | Remove plywood sheathing at Roof D | [Sheet A1.1 Note 9]
|  | Demolition: | Remove BUR, cant strips, and tapered insulation |  |  | 10
|  |  | Remove coping and associated hardware |  |  | 11000
|  |  | Remove existing scuppers (Save Roof B for replacement) |  |  | 50
Remove existing access ladder
Remove wood privacy fence
Remove sloped 2x4 sleepers (Roof D)
Remove plywood sheathing at Roof D
|  |  |  | Demolition (ALL) |  | 11060

## Architectural - New Constructio
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
ARC-08 | Arch | Roof System (A-H) | Install | Fully Adhered EPDM/TPO per spec | [Sheet A1.2]
ARC-09 | Arch | Coverboard | Install | New 5/8" coverboard over existing sheathing | [Detail 4/A2.3]
ARC-10 | Arch | Tapered Insulation | Install | Crickets: 1/2" per 12" slope to drains | [Sheet A1.2 Note 8]
ARC-11 | Arch | Parapet Framing | Framing | Sister new 2x4 framing to existing; Match height | [Detail 2/A2.1]
ARC-12 | Arch | Parapet Sheathing | Install | New 1/2" plywood sheathing | [Detail 2/A2.1]
ARC-13 | Arch | Metal Flashing | Install | 24 ga. pre-finished flashing; Continuous hold-down cleats | [Detail 2/A2.1]
ARC-14 | Arch | Composite Trim | Install | 1x8 over 1x10 composite trim | [Detail 2/A2.1]
ARC-15 | Arch | Roof Scupper | Install | New pre-manufactured scupper (Detail 5/A2.3) | [Sheet A1.2]
ARC-16 | Arch | Roof Hatch | Install | 30"x54" Hatch; Insulated; Padlock hasp | [Sheet A1.2]
ARC-17 | Arch | Roof Ladder | Install | Aluminum; Serrated rungs; Wall brackets | [Detail 6/A2.3]
ARC-18 | Arch | Walking Pads | Install | Rubber walking mats (Hatch to Ladder/Equipment) | [Sheet A1.2 Note 10]
Fully Adhered EPDM/TPO per spec
New 5/8" coverboard over existing sheathing
Crickets: 1/2" per 12" slope to drains
Sister new 2x4 framing to existing; Match height
New 1/2" plywood sheathing
24 ga. pre-finished flashing; Continuous hold-down cleats
1x8 over 1x10 composite trim
New pre-manufactured scupper (Detail 5/A2.3)
30"x54" Hatch; Insulated; Padlock hasp
Aluminum; Serrated rungs; Wall brackets
Rubber walking mats (Hatch to Ladder/Equipment)

## Mechanical - HVAC Equipment
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
MEC-01 | Mech | RTU-1 (Raquetball) | Install | 4 Ton; Daikin 048; Gas/Electric | [Sheet M0.1]
MEC-02 | Mech | RTU-2 (Cardio) | Install | 3 Ton; Daikin 036; Gas/Electric | [Sheet M0.1]
MEC-03 | Mech | RTU-3 (Commons) | Install | 8.5 Ton; Daikin 102; Gas/Electric | [Sheet M0.1]
MEC-04 | Mech | RTU-4 (Lobby) | Install | 8.5 Ton; Daikin 102; Gas/Electric | [Sheet M0.1]
MEC-05 | Mech | RTU-5 (Lockers) | Install | 7.5 Ton; Daikin 090; Gas/Electric | [Sheet M0.1]
MEC-06 | Mech | RTU-6 (Gym) | Install | 20 Ton; Daikin 240; Gas/Electric | [Sheet M0.1]
MEC-07 | Mech | Exhaust Fan EF-1 | Install | Ceiling Mount; 200 CFM | [Sheet M0.1]
MEC-08 | Mech | Exhaust Fan EF-2 | Install | Ceiling Mount; 200 CFM | [Sheet M0.1]
MEC-09 | Mech | Exhaust Fan EF-3 | Install | Inline; 400 CFM | [Sheet M0.1]
MEC-10 | Mech | Exhaust Fan EF-4 | Install | Roof Direct; 720 CFM | [Sheet M0.1]
MEC-11 | Mech | Exhaust Fan EF-5 | Install | Roof Direct; 6280 CFM; 3 HP | [Sheet M0.1]
MEC-12 | Mech | Roof Curbs (RTU) | Install | 24" High Insulated Curb; Coordinate w/ Structural | [Sheet M0.1 Note 2]
MEC-13 | Mech | Roof Curbs (EF) | Install | Prefabricated metal curb per spec | [Detail 4/A2.3]

## Mechanical - Ductwork & Gas
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
MEC-14 | Mech | Ductwork (Interior) | Install | Galvanized Steel; SMACNA Std; 2" w.g. class | [Sheet M0.2]
MEC-15 | Mech | Ductwork (Exterior) | Install | Q-Duct Phenolic Pre-insulated (R-12); Weatherproof | [Sheet M0.2]
MEC-16 | Mech | Duct Insulation | Install | 2" Glass Fiber Foil Faced (Supply/Outside Air) | [Sheet M0.2]
MEC-17 | Mech | Duct Lining | Install | 1" Rigid Glass Fiber (Return/Drops) | [Sheet M0.2]
MEC-18 | Mech | Doghouse | Fabricate | 32"x32"x24" Insulated Doghouse for duct penetrations | [Sheet M2.3]
MEC-19 | Mech | Gas Piping | Demo | Remove existing black steel pipe on roof | [Sheet M1.2]
MEC-20 | Mech | Gas Piping | Install | 1-1/4", 1", 2" Black Steel; Supports; Paint | [Sheet M2.3]
MEC-21 | Mech | Seismic Bracing | Install | Brace all equipment per IBC 2009 | [Sheet E4.0 Note 6]

## Plumbing
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
PLU-01 | Plumb | Roof Drains (RD-1) | Install | Cast Iron dome; 3" connection | [Sheet M0.1]
PLU-02 | Plumb | Overflow Drains (OD-1) | Install | 2" Water Dam Collar; 3" connection | [Sheet M0.1]
PLU-03 | Plumb | Rain Leader Piping | Install | 3" & 4" Cast Iron (No-Hub) or ABS (concealed only) | [Sheet M2.2]
PLU-04 | Plumb | Pipe Insulation | Install | 1" Fiberglass w/ ASJ | [Sheet M0.2]
PLU-05 | Plumb | Heat Trace (Plumb) | Install | Electric heat trace in rain leaders (Coordinate w/ Elec) | [Sheet C1.0]
PLU-06 | Plumb | Downspout Nozzle | Install | Set in sealant at exterior siding | [Detail 9/A2.2]
PLU-07 | Plumb | Cleanouts | Install | Wall/Floor cleanouts as indicated | [Sheet M2.2]

## Electrical
ID | Trade | Work Package / Item | Action | Specifications / Notes | Source Ref
ELE-01 | Elec | Panel 'X' | Demolish | Remove panel and associated feeders/conduit | [Sheet E1.0]
ELE-02 | Elec | Panel 'D' | Install | New Panel; Relocate existing circuits | [Sheet E1.0]
ELE-03 | Elec | Main Distribution | Upgrade | Replace 300A Main with 400A Main Breaker | [Sheet E4.0]
ELE-04 | Elec | Feeders (Panel A) | Replace | 1-1/4" C, 3#2, #2N, #8G | [Sheet E4.0]
ELE-05 | Elec | Feeders (Panel MECH) | New | 4" C, 3#500kcmil, #500kcmil N, #2G | [Sheet E4.0]
ELE-06 | Elec | RTU Connections | Install | Power connections to 6 RTUs (Disconnects/Fuses) | [Sheet E3.0]
ELE-07 | Elec | Smoke Detectors | Install | Duct detectors for RTUs > 2000 CFM (RTU-3,4,5,6) | [Sheet E3.0 Note 2]
ELE-08 | Elec | Heat Trace Power | Install | Connection kit; Thermostat; J-box; Pilot light | [Sheet E4.0]
ELE-09 | Elec | Audio/Visual Alarm | Install | For smoke detector; Locate at check-in counter | [Sheet E3.0 Note 2]
ELE-10 | Elec | Disconnect Switches | Install | NEMA 3R (Roof); Fused/Non-fused as required | [Sheet E4.0]
ELE-11 | Elec | Convenience Outlets | Install | GFCI outlets at RTUs (115V) | [Sheet M0.1 Note 3]
ELE-12 | Elec | Labeling | Admin | Update circuit directories; Label new panels | [Sheet E4.0 Note 18]

## Additional Work Packages Identi
ID | Trade | Work Package / Item | Action | Specs / Quantities | Source Ref
ARC-19 | Arch | Composite Siding & Trim | Install | CertainTeed "Cedar Texture" 7 1/4"; ColorMax finish | [Spec 07 46 40]
ARC-20 | Arch | Roof Hatch Safety Rail | Install | Bilco "Bil-Guard" Fixed Railing System; Safety Yellow | [Spec 07 72 10] | note: after reviewing all project documents and not only the design documents the following additions to work packages were detected and in the next tab changes to inital work packages
ARC-21 | Arch | Painting (Exterior) | Paint | ICI Paints; 2 coats over primer; Composite Trim & Ferrous Metals | [Spec 09 90 00]
ARC-22 | Arch | Painting (Interior) | Paint | ICI Paints; General Drywall; Eggshell finish | [Spec 09 90 00]
ARC-23 | Arch | Joint Sealants | Install | Silicone (Dow 795) & Polyurethane (Tremco Dymeric); Color selected by Arch | [Spec 07 90 00]
ARC-24 | Arch | Wood Decking | Repair | 4" x 6" T&G Douglas Fir Decking (Match Existing) | [Spec 06 01 00]
CIV-14 | Civil | Asphalt Paving | Install | ADOT&PF Class 'A', Type II Aggregate; Temp > 45°F | [Spec 32 12 16]
CIV-15 | Civil | Leveling Course | Install | Grading D-1; Compact to 95% density | [Spec 32 12 16]
GEN-07 | General | Temporary Facilities | Install | Temp heat, power, sanitary facilities, & field office | [Spec 01 50 00]
GEN-08 | General | Project Signage | Install | Project identification sign; Maintain cleanliness | [Spec 01 50 00]
GEN-09 | General | Final Cleaning | Service | Remove waste, foreign matter, stains; Polish glass | [Spec 01 71 00]
MEC-16 | Mech | HVAC Controls | Install | Factory controls, wall timer, or time clock ONLY (No DDC) | [Addendum 1]
MEC-17 | Mech | Duct Smoke Detectors | Install | Required for RTUs > 2000 CFM (RTU-3, 4, 5, 6) | [Gen Cond 4.11]
MEC-18 | Mech | Testing & Balancing | Service | Independent AABC or NEBB certified agency | [Spec 01 67 00]
ELE-13 | Elec | Temp Power/Lighting | Install | 2 watts/sq ft min illumination; Maintain safe wiring | [Spec 01 50 00]
ELE-14 | Elec | Heat Trace Connection | Install | Connection for rain leaders (Coordinate w/ Civil) | [Sheet C1.0]
BID-01 | Admin | Performance Bond | Admin | 100% of Contract Amount | [ITB Sec 5]
BID-02 | Admin | Insurance | Admin | Comm. Gen Liability $1M; Auto $1M; Work Comp | [Gen Cond 7.2]

## Critical Updates to Existing Sc
ID | Work Package | Previous Value (Plans) | Updated Value (Specs/Addenda) | Reason
ARC-02 | Roof Recovery Board | 5/8" Coverboard (Generic) | 5/8" Georgia Pacific Dens Deck | [Addendum 2]: Required for 20yr/120mph Warranty.
MEC-12 | RTU-5 Curb | Standard Curb | Field Fabricated Curb | [Addendum 1]: Specific instruction to meet design intent.
MEC-01 | RTU-1 (Racquetball) | Base Bid | Additive Alternate #1 | [Bid Form]: Defined as Alt #1.
MEC-06 | RTU-6 (Gym) | Base Bid | Additive Alternate #2 | [Bid Form]: Defined as Alt #2.
MEC-XX | HVAC Mfrs | Daikin (Basis of Design) | York, Rupp Air, Nailor added | [Addendum 1]: Approved substitutions listed.
PLU-03 | Rain Leaders | Cast Iron or ABS | Ductile Iron CL52 (Exterior) | [Spec 33 41 00]: Specific material for rain leaders.
GEN-XX | Bid Deadline | 2023-03-23 | 2023-03-28 | [Addendum 2]: Extension granted.
note: here are changes to initially extracted work packages after reading all the project documents and not just the design document (previous tab shows added changes)

## annotation detection
1. Sheet C1.0 (Civil Site) Layer: Excavation Highlight: Box [CIV-01] over the large drain field area. Tag: "Scope: Excavate 30x15x3.5. Note: Unknown Utilities Risk." Highlight: Polygon [CIV-03] over the sidewalk at Bidarka St. Tag: "Scope: Demo & Pour 4in Concrete." 2. Sheet A1.2 (New Roof) Layer: Roofing Highlight: Shading over Roofs A, B, C, D, E, F, G, H. Tag: [ARC-02] "Install EPDM/TPO System." Highlight: Symbol [ARC-04] at Hatch location. Tag: "New Roof Hatch (30x54)." 3. Sheet M2.3 (Mech Roof) Layer: HVAC Highlight: Boxes over RTU-1 through RTU-6. Tag: [MEC-01 to MEC-06] "Replace Unit & Curb. Gas Connection [MEC-13] Required." Highlight: Square [MEC-15] near RTU-6. Tag: "Doghouse Penetration for Ductwork." 4. Sheet E4.0 (One-Line) Layer: Distribution Highlight: "Main MB" symbol. Tag: [ELE-03] "Upsize to 400A." Highlight: Feeders to Panel MECH. Tag: [ELE-04] "New 4in Conduit Run."

## AI insights
Conflict Detected: The Civil sheet calls for Heat Trace in rain leaders, and the Electrical sheet confirms the connection. The AI successfully linked these two separate trade drawings.
Missing Detail Warning: The Civil drawing mentions "Remove & Replace Asphalt", but no specific asphalt thickness is listed in the Extraction table, only "Match Existing Drainage Patterns". User Action: Verify asphalt spec.